## Instructions
SunSpec PICS Template
This SunSpec PICS template was generated by SunSpec Dashboard v1.0.6 based on the model contents of the connected device.
Most of the necessary information is populated but the PICS must be completed before submission by performing the following steps:
1. Examine the entry in the 'Value' column for each point to verify correctness:
- Common model (1) points that are implemented should contain the current value.
- All other model points that are implemented and have a variable value should contain the string 'supported'.
- All other model points that are implemented and have a constant value should contain the constant value.
It is assumed that scale factors are constants. If they are not, change the value to 'supported'.
- All unimplemented points should contain the string 'unimplemented'.
- For each enumeration or bit field entry that is not implemented, change the string to 'unimplemented'.
2. Examine the 'R/W' column to ensure the access is correct. It should be either 'R' or 'RW'.
3. For any point that has an implementation deviation or special considerations indicate the issue in the 'Conformance Notes' column.
The certificate number will be filled in when certification is complete and this file will be archived with the Testing Info tab removed
along with a copy of the certificate on sunspec.org.

## Certification Info
Certificate Number | SM-000009
Location | https://sunspec.org/wp-content/uploads/2020/11/SunSpec-Altenergy-certificate-SM000009.pdf
Date | 2020-11-12 15:36:48
Manufacturer Name | Altenergy Power System Inc.
Product Name | Microinverter；APpcs
Product Models | YC600,YC600B,QS1,QS1A,YC250A,YC250I,YC500A,YC500I，YC500A-127,YC500I-127，HDMI330A，DS3,SS3，SS3X,SS3L,SS3H，DS3X，DS3L，DS3H，DS3D；APpcs，APpcs-2K5，APpcs-3K，APpcs-5K
Product Description | Microinverter；APpcs

## Testing Info
Submitter | kevin.lu
Email | kevin.lu@apsystems.cn
Phone | 0573-82583529
Interface Type | RTU
Baud Rate | 9600
Slave Id | 1

## 1
Hex Address | Address | Point | Index | Subvalue | Value | Type | R/W | Conformance Notes
9C42 | 40002 | ID |  |  | 1 | uint16 | R
9C43 | 40003 | L |  |  | 66 | uint16 | R
9C44 | 40004 | Manufacturer (Mn) |  |  | APsystems | string | R
9C54 | 40020 | Model (Md) |  |  | YC600 | string | R
9C64 | 40036 | Options (Opt) |  |  | unimplemented | string | R
9C6C | 40044 | Version (Vr) |  |  | V0 | string | R
9C74 | 40052 | Serial Number (SN) |  |  | 409000064675 | string | R
9C84 | 40068 | Device Address (DA) |  |  | 1 | uint16 | RW
9C85 | 40069 | Pad |  |  |  | pad | R

## 101
| Hex Address | Address | Point | Index | Subvalue | Value | Type | R/W | Conformance Notes
9C86 | 9C86 | 40070 | ID |  |  | 101 | uint16
9C87 | 9C87 | 40071 | L |  |  | 50 | uint16
9C88 | 9C88 | 40072 | Amps (A) |  |  | supported | uint16 | R
9C89 | 9C89 | 40073 | Amps PhaseA (AphA) |  |  | supported | uint16 | R
9C8A | 9C8A | 40074 | Amps PhaseB (AphB) |  |  | unimplemented |  | R
9C8B | 9C8B | 40075 | Amps PhaseC (AphC) |  |  | unimplemented |  | R
9C8C | 9C8C | 40076 | A_SF |  |  | -2 | sunssf | R
9C8D | 9C8D | 40077 | Phase Voltage AB (PPVphAB) |  |  | unimplemented |  | R
9C8E | 9C8E | 40078 | Phase Voltage BC (PPVphBC) |  |  | unimplemented |  | R
9C8F | 9C8F | 40079 | Phase Voltage CA (PPVphCA) |  |  | unimplemented |  | R
9C90 | 9C90 | 40080 | Phase Voltage AN (PhVphA) |  |  | supported | uint16 | R
9C91 | 9C91 | 40081 | Phase Voltage BN (PhVphB) |  |  | unimplemented |  | R
9C92 | 9C92 | 40082 | Phase Voltage CN (PhVphC) |  |  | unimplemented |  | R
9C93 | 9C93 | 40083 | V_SF |  |  | -1 | sunssf | R
9C94 | 9C94 | 40084 | Watts (W) |  |  | supported | uint16 | R
9C95 | 9C95 | 40085 | W_SF |  |  | -1 | sunssf | R
9C96 | 9C96 | 40086 | Hz |  |  | supported | uint16 | R
9C97 | 9C97 | 40087 | Hz_SF |  |  | -2 | sunssf | R
9C98 | 9C98 | 40088 | VA |  |  | supported | uint16 | R
9C99 | 9C99 | 40089 | VA_SF |  |  | -1 | sunssf | R
9C9A | 9C9A | 40090 | VAr |  |  | supported | uint16 | R
9C9B | 9C9B | 40091 | VAr_SF |  |  | -1 | sunssf | R
9C9C | 9C9C | 40092 | PF |  |  | supported | uint16 | R
9C9D | 9C9D | 40093 | PF_SF |  |  | -3 | sunssf | R
9C9E | 9C9E | 40094 | WattHours (WH) |  |  | supported | uint16 | R
9CA0 | 9CA0 | 40096 | WH_SF |  |  | 0 | sunssf | R
9CA1 | 9CA1 | 40097 | DC Amps (DCA) |  |  | unimplemented |  | R
9CA2 | 9CA2 | 40098 | DCA_SF |  |  | unimplemented |  | R
9CA3 | 9CA3 | 40099 | DC Voltage (DCV) |  |  | unimplemented |  | R
9CA4 | 9CA4 | 40100 | DCV_SF |  |  | unimplemented |  | R
9CA5 | 9CA5 | 40101 | DC Watts (DCW) |  |  | unimplemented |  | R
9CA6 | 9CA6 | 40102 | DCW_SF |  |  | unimplemented |  | R
9CA7 | 9CA7 | 40103 | Cabinet Temperature (TmpCab) |  |  | supported | int6 | R
9CA8 | 9CA8 | 40104 | Heat Sink Temperature (TmpSnk) |  |  | unimplemented |  | R
9CA9 | 9CA9 | 40105 | Transformer Temperature (TmpTrns) |  |  | unimplemented |  | R
9CAA | 9CAA | 40106 | Other Temperature (TmpOt) |  |  | unimplemented |  | R
9CAB | 9CAB | 40107 | Tmp_SF |  |  | -1 | sunssf | R
9CAC | 9CAC | 40108 | Operating State (St) |  |  | supported | enum16 | R
[5 empty] | Off (OFF) | 1
[5 empty] | Sleeping (SLEEPING) | 2
[5 empty] | Starting (STARTING) | 3
[5 empty] | MPPT | 4
[5 empty] | Throttled (THROTTLED) | 5
[5 empty] | Shutting down (SHUTTING_DOWN) | 6
[5 empty] | Fault (FAULT) | 7
[5 empty] | Standby (STANDBY) | 8
9CAD | 9CAD | 40109 | Vendor Operating State (StVnd) |  |  | unimplemented |  | R
9CAE | 9CAE | 40110 | Event1 (Evt1) |  |  | supported | bitfield32 | R
[5 empty] | Ground fault (GROUND_FAULT) | 0
[5 empty] | DC over voltage (DC_OVER_VOLT) | 1
[5 empty] | AC disconnect open (AC_DISCONNECT) | 2
[5 empty] | DC disconnect open (DC_DISCONNECT) | 3
[5 empty] | Grid disconnect (GRID_DISCONNECT) | 4
[5 empty] | Cabinet open (CABINET_OPEN) | 5
[5 empty] | Manual shutdown (MANUAL_SHUTDOWN) | 6
[5 empty] | Over temperature (OVER_TEMP) | 7
[5 empty] | Frequency above limit (OVER_FREQUENCY) | 8
[5 empty] | Frequency under limit (UNDER_FREQUENCY) | 9
[5 empty] | AC Voltage above limit (AC_OVER_VOLT) | 10
[5 empty] | AC Voltage under limit (AC_UNDER_VOLT) | 11
[5 empty] | Blown String fuse on input (BLOWN_STRING_FUSE) | 12
[5 empty] | Under temperature (UNDER_TEMP) | 13
[5 empty] | Generic Memory or Communication error (internal) (MEMORY_LOSS) | 14
[5 empty] | Hardware test failure (HW_TEST_FAILURE) | 15
9CB0 | 9CB0 | 40112 | Event Bitfield 2 (Evt2) |  |  | unimplemented |  | R
9CB2 | 9CB2 | 40114 | Vendor Event Bitfield 1 (EvtVnd1) |  |  | unimplemented |  | R
9CB4 | 9CB4 | 40116 | Vendor Event Bitfield 2 (EvtVnd2) |  |  | unimplemented |  | R
9CB6 | 9CB6 | 40118 | Vendor Event Bitfield 3 (EvtVnd3) |  |  | unimplemented |  | R
9CB8 | 9CB8 | 40120 | Vendor Event Bitfield 4 (EvtVnd4) |  |  | unimplemented |  | R

## 111
Hex Address | Address | Point | Index | Subvalue | Value | Type | R/W | Conformance Notes
9CBA | 40122 | ID |  |  | 111 | uint16
9CBB | 40123 | L |  |  | 60 | uint16
9CBC | 40124 | Amps (A) |  |  | supported | float32 | R
9CBE | 40126 | Amps PhaseA (AphA) |  |  | supported | float32 | R
9CC0 | 40128 | Amps PhaseB (AphB) |  |  | unimplemented | float32 | R
9CC2 | 40130 | Amps PhaseC (AphC) |  |  | unimplemented | float32 | R
9CC4 | 40132 | Phase Voltage AB (PPVphAB) |  |  | unimplemented | float32 | R
9CC6 | 40134 | Phase Voltage BC (PPVphBC) |  |  | unimplemented | float32 | R
9CC8 | 40136 | Phase Voltage CA (PPVphCA) |  |  | unimplemented | float32 | R
9CCA | 40138 | Phase Voltage AN (PhVphA) |  |  | supported | float32 | R
9CCC | 40140 | Phase Voltage BN (PhVphB) |  |  | unimplemented | float32 | R
9CCE | 40142 | Phase Voltage CN (PhVphC) |  |  | unimplemented | float32 | R
9CD0 | 40144 | Watts (W) |  |  | supported | float32 | R
9CD2 | 40146 | Hz |  |  | supported | float32 | R
9CD4 | 40148 | VA |  |  | supported | float32 | R
9CD6 | 40150 | VAr |  |  | supported | float32 | R
9CD8 | 40152 | PF |  |  | supported | float32 | R
9CDA | 40154 | WattHours (WH) |  |  | supported | float32 | R
9CDC | 40156 | DC Amps (DCA) |  |  | unimplemented | float32 | R
9CDE | 40158 | DC Voltage (DCV) |  |  | unimplemented | float32 | R
9CE0 | 40160 | DC Watts (DCW) |  |  | unimplemented | float32 | R
9CE2 | 40162 | Cabinet Temperature (TmpCab) |  |  | supported | float32 | R
9CE4 | 40164 | Heat Sink Temperature (TmpSnk) |  |  | unimplemented |  | R
9CE6 | 40166 | Transformer Temperature (TmpTrns) |  |  | unimplemented |  | R
9CE8 | 40168 | Other Temperature (TmpOt) |  |  | unimplemented |  | R
9CEA | 40170 | Operating State (St) |  |  | unimplemented |  | R
|  |  |  | ggOFF | supported
|  |  |  | ggSLEEPING | supported
|  |  |  | ggSTARTING | supported
|  |  |  | MPPT (ggMPPT) | supported
|  |  |  | ggTHROTTLED | supported
|  |  |  | ggSHUTTING_DOWN | supported
|  |  |  | ggFAULT | supported
|  |  |  | ggSTANDBY | supported
|  |  |  | Off (None) | supported
|  |  |  | Sleeping (None) | supported
|  |  |  | Starting (None) | supported
|  |  |  | Throttled (None) | supported
|  |  |  | Shutting down (None) | supported
|  |  |  | Fault (None) | supported
|  |  |  | Standby (None) | supported
9CEB | 40171 | Vendor Operating State (StVnd) |  |  | unimplemented |  | R
9CEC | 40172 | Event1 (Evt1) |  |  | unimplemented |  | R
|  |  |  | Ground fault (GROUND_FAULT) | supported
|  |  |  | DC over voltage (DC_OVER_VOLT) | supported
|  |  |  | AC disconnect open (AC_DISCONNECT) | supported
|  |  |  | DC disconnect open (DC_DISCONNECT) | supported
|  |  |  | Grid shutdown (GRID_DISCONNECT) | supported
|  |  |  | Cabinet open (CABINET_OPEN) | supported
|  |  |  | Manual shutdown (MANUAL_SHUTDOWN) | supported
|  |  |  | Over temperature (OVER_TEMP) | supported
|  |  |  | Frequency above limit (OVER_FREQUENCY) | supported
|  |  |  | Frequency under limit (UNDER_FREQUENCY) | supported
|  |  |  | AC Voltage above limit (AC_OVER_VOLT) | supported
|  |  |  | AC Voltage under limit (AC_UNDER_VOLT) | supported
|  |  |  | Blown String fuse on input (BLOWN_STRING_FUSE) | supported
|  |  |  | Under temperature (UNDER_TEMP) | supported
|  |  |  | Generic Memory or Communication error (internal) (MEMORY_LOSS) | supported
|  |  |  | Hardware test failure (HW_TEST_FAILURE) | supported
9CEE | 40174 | Event Bitfield 2 (Evt2) |  |  | unimplemented |  | R
9CF0 | 40176 | Vendor Event Bitfield 1 (EvtVnd1) |  |  | unimplemented |  | R
9CF2 | 40178 | Vendor Event Bitfield 2 (EvtVnd2) |  |  | unimplemented |  | R
9CF4 | 40180 | Vendor Event Bitfield 3 (EvtVnd3) |  |  | unimplemented |  | R
9CF6 | 40182 | Vendor Event Bitfield 4 (EvtVnd4) |  |  | unimplemented |  | R

## 123
Hex Address | Address | Point | Index | Subvalue | Value | Type | R/W | Conformance Notes
9CF8 | 40184 | ID |  |  | 123 | uint | R | Immediate Inverters Controls
9CF9 | 40185 | L |  |  | 24 | uint | R | Model Length
9CFA | 40186 | Conn_WinTms |  |  | unimplemented |  | RW
9CFB | 40187 | Conn_RvrtTms |  |  | unimplemented |  | RW
9CFC | 40188 | Conn |  |  | supported |  | RW | Enumerated valued. Connection control
|  |  |  | DISCONNECT | supported
|  |  |  | CONNECT | supported
9CFD | 40189 | WMaxLimPct |  |  | supported |  | RW | Set power output to specified level
9CFE | 40190 | WMaxLimPct_WinTms |  |  | unimplemented |  | RW
9CFF | 40191 | WMaxLimPct_RvrtTms |  |  | unimplemented |  | RW
9D00 | 40192 | WMaxLimPct_RmpTms |  |  | unimplemented |  | RW
9D01 | 40193 | WMaxLim_Ena |  |  | supported |  | RW | Enumerated valued. Throttle enable/disable control
|  |  |  | DISABLED | supported
|  |  |  | ENABLED | supported
9D02 | 40194 | OutPFSet |  |  | unimplemented |  | RW
9D03 | 40195 | OutPFSet_WinTms |  |  | unimplemented |  | RW
9D04 | 40196 | OutPFSet_RvrtTms |  |  | unimplemented |  | RW
9D05 | 40197 | OutPFSet_RmpTms |  |  | unimplemented |  | RW
9D06 | 40198 | OutPFSet_Ena |  |  | unimplemented |  | RW
|  |  |  | DISABLED | supported
|  |  |  | ENABLED | supported
9D07 | 40199 | VArWMaxPct |  |  | unimplemented |  | RW
9D08 | 40200 | VArMaxPct |  |  | unimplemented |  | RW
9D09 | 40201 | VArAvalPct |  |  | unimplemented |  | RW
9D0A | 40202 | VArPct_WinTms |  |  | unimplemented |  | RW
9D0B | 40203 | VArPct_RvrtTms |  |  | unimplemented |  | RW
9D0C | 40204 | VArPct_RmpTms |  |  | unimplemented |  | RW
9D0D | 40205 | VArPct_Mod |  |  | unimplemented |  | RW
|  |  |  | NONE | supported
|  |  |  | WMax | supported
|  |  |  | VArMax | supported
|  |  |  | VArAval | supported
9D0E | 40206 | VArPct_Ena |  |  | unimplemented |  | RW
|  |  |  | DISABLED | supported
|  |  |  | ENABLED | supported
9D0F | 40207 | WMaxLimPct_SF |  |  | -1 |  | R
9D10 | 40208 | OutPFSet_SF |  |  | -1 |  | R
9D11 | 40209 | VArPct_SF |  |  | -1 |  | R

## 114
Hex Address | Address | Point | Index | Subvalue | Value | Type | R/W | Conformance Notes
9D14 | 40212 | ID |  |  | 114
9D15 | 40213 | L |  |  | 48
9D16 | 40214 | DC Voltage (DCV1) |  |  | supported | float32 | R
9D18 | 40216 | DC Voltage (DCV2) |  |  | supported | float32 | R
9D1A | 40218 | DC Voltage (DCV3) |  |  | Depends on model | float32 | R
9D1C | 40220 | DC Voltage (DCV4) |  |  | Depends on model | float32 | R
9D1E | 40222 | DC Voltage (DCV5) |  |  | Depends on model | float32 | R
9D20 | 40224 | DC Voltage (DCV6) |  |  | Depends on model | float32 | R
9D22 | 40226 | DC Voltage (DCV7) |  |  | Depends on model | float32 | R
9D24 | 40228 | DC Voltage (DCV8) |  |  | Depends on model | float32 | R
9D26 | 40230 | DC Amps (DCA1) |  |  | supported | float32 | R
9D28 | 40232 | DC Amps (DCA2) |  |  | supported | float32 | R
9D2A | 40234 | DC Amps (DCA3) |  |  | Depends on model | float32 | R
9D2C | 40236 | DC Amps (DCA4) |  |  | Depends on model | float32 | R
9D2E | 40238 | DC Amps (DCA5) |  |  | Depends on model | float32 | R
9D30 | 40240 | DC Amps (DCA6) |  |  | Depends on model | float32 | R
9D32 | 40242 | DC Amps (DCA7) |  |  | Depends on model | float32 | R
9D34 | 40244 | DC Amps (DCA8) |  |  | Depends on model | float32 | R
9D36 | 40246 | DC Watts (DCW1) |  |  | supported | float32 | R
9D38 | 40248 | DC Watts (DCW2) |  |  | supported | float32 | R
9D3A | 40250 | DC Watts (DCW3) |  |  | Depends on model | float32 | R
9D3C | 40252 | DC Watts (DCW4) |  |  | Depends on model | float32 | R
9D3E | 40254 | DC Watts (DCW5) |  |  | Depends on model | float32 | R
9D40 | 40256 | DC Watts (DCW6) |  |  | Depends on model | float32 | R
9D42 | 40258 | DC Watts (DCW7) |  |  | Depends on model | float32 | R
9D44 | 40260 | DC Watts (DCW8) |  |  | Depends on model | float32 | R